## Input
Machined Venturi
Fluid | Gas |  |  |  |  | 'As Cast' Venturi
Operating Pressure | 5000000 | Pa[A]
Operating Temperature | 294.26 | °K
Operating Density | 1.066 | kg/m3
Compressibility | 0.997
Operating Viscosity | 1.8e-05 | Pa.s
Isentropic Index | 1.4
Flowrate | 3 | kg/s |  |  | 0.8
Materials | Pipe | 1.353e-05
| Element (Throat) | 1.789e-05
Pipe ID | 0.25451 | m
DP | 25000 | Pa[A] | Throat Bore | 0.12728 | m
.
Convert Operating Pressure | 5000000 | Pa[A]
Convert temperature | 294.26 | °K
Calculate mass flow (if not given) | 3 | kg/s
Calc/convert density | 1.066 | kg/m³
Convert diameter with expans. | 0.25452 | m
Calc pipe area | 0.050877 | m2
Calc pipe velocity | 55.3152 | m/s
Calculate viscosity | 1.8e-05 | Pa.s
Calc Reynolds Number | 833765.7062

## Nozzle ISA 1932
CALCULATION TYPE | ISO 5167:2003 |  |  | ISA 1932 Nozzle "N2"
Convert Operating Pressure | 5000000 | Pa[A]
Convert temperature | 294.26 | °K
Calculate mass flow (if not given) | 3 | kg/s
Calc/convert density | 1.066 | kg/m³
Convert diameter with expans. | 0.25452 | m
Calc pipe area | 0.050877 | m2
Calc pipe velocity | 55.3152 | m/s
Calculate viscosity | 1.8e-05 | Pa.s
Calc Reynolds Number | 833765.7062
Size By Bore
P2/P1 | 0.995 |  |  |  | Sizing Factor, SM | 0.25541
DP | 25000 | Pa[A] |  |  | Machined Bore | 0.12728
Downstream Pressure, P2 | 4975000 | Pa[A] |  |  | Operating Bore | 0.12729 | m
Operting Bore | 0.12823 | m |  |  | Beta, β0 | 0.50012
Machined Bore | 0.12823 | m |  |  | A | 0.027888
[5 empty] | Uncertainty C | If β2 =<0.6 then 0.8% / If β2 >0.6 then (2*β-0.4) in %
[5 empty] | Relative Uncertainty Y | 0.01029% | +-
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  |  | Co-efficient of Discharge, C | 0.97645 | If β2 =<0.6 then 0.8% / If β2 >0.6 then (2*β-0.4) in % | +-
Sizing Factor, SM | 0.25541 |  |  |  | Initial Expansibility Factor, Y | 0.99708 | 0.01029% | +-
Initial Beta, β | 0.49804 |  |  |  | Beta, β | 0.50374
[5 empty] | E | 1.0328
Co-efficient of Discharge, C0 | 0.97667
Expansibility Factor, Y0 | 0.99708
Beta, β0 | 0.50368
Co-efficient of Discharge, C1 | 0.97606
Expansibility Factor, Y1 | 0.99707
Beta, β1 | 0.50383
Co-efficient of Discharge, C₂ | 0.97604
Expansibility Factor, Y₂ | 0.99707
Beta, β₂ | 0.50384
Uncertainty C₃ | If β2 =<0.6 then 0.8% / If β2 >0.6 then (2*β-0.4) in %
Relative Uncertainty Y₃ | 0.01%
Co-efficient of Discharge, C₃ | 0.97604 | If β2 =<0.6 then 0.8% / If β2 >0.6 then (2*β-0.4) in %
E | 1.0339 |  |  |  | Differential Pressure, Δp | 25731.6836 | Pa[A]
Expansibility Factor, Y₃ | 0.99707 | 0.01% | +-
Beta, β₃ | 0.50384
Pressure Loss | 15059.3666 | Pa[A]
[5 empty] | Differential Pressure, Δp | 25731.6836 | Pa[A]
Machined Bore (mm) | 128.2318 | mm |  |  |  | 127.2849
Operting Bore | 128.2343 | mm |  |  | Operting Bore | 127.2875 | mm
qm | 2.9999 | kg/s |  |  | qm | 2.9971 | kg/s

## Long Radius Nozzle
CALCULATION TYPE | ISO 5167:2003 |  |  | Long Radius Nozzle "N3"
Convert Operating Pressure | 5000000 | Pa[A]
Convert temperature | 294.26 | °K
Calculate mass flow (if not given) | 3 | kg/s
Calc/convert density | 1.066 | kg/m³
Convert diameter with expans. | 0.25452 | m
Calc pipe area | 0.050877 | m2
Calc pipe velocity | 55.3152 | m/s
Calculate viscosity | 1.8e-05 | Pa.s
Calc Reynolds Number | 833765.7062
Size By Bore
P2/P1 | 0.995 |  |  |  | Sizing Factor, SM | 0.25541
DP | 25000 | Pa[A] |  |  | Machined Bore | 0.12728
Downstream Pressure, P2 | 4975000 | Pa[A] |  |  | Operating Bore | 0.12729 | m
Operting Bore | 0.1273 | m |  |  | Beta, β0 | 0.50012
Machined Bore | 0.12729 | m |  |  | A | 0.027888
[5 empty] | Uncertainty C | If β2 =<0.6 then 0.8% / If β2 >0.6 then (2*β-0.4) in %
[5 empty] | Relative Uncertainty Y | 0.01% | +-
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  |  | Co-efficient of Discharge, C | 0.99144 | If β2 =<0.6 then 0.8% / If β2 >0.6 then (2*β-0.4) in % | +-
Sizing Factor, SM | 0.25541 |  |  |  | Initial Expansibility Factor, Y | 0.99708 | 0.01% | +-
Initial Beta, β | 0.49804 |  |  |  | Beta, β | 0.50015
| 0.027796 |  |  |  | E | 1.0328
Co-efficient of Discharge, C0 | 0.99145
Expansibility Factor, Y0 | 0.99708
Beta, β0 | 0.50015
0.02789
Co-efficient of Discharge, C1 | 0.99144
Expansibility Factor, Y1 | 0.99708
Beta, β1 | 0.50015
0.02789
Co-efficient of Discharge, C₂ | 0.99144
Expansibility Factor, Y₂ | 0.99708
Beta, β₂ | 0.50015
Uncertainty C₃ | If β =>2 and =<0.8 then uncertainty = 2.0%
Relative Uncertainty Y₃ | 0.01%
Co-efficient of Discharge, C₃ | 0.99144 | If β =>2 and =<0.8 then uncertainty = 2.0%
E | 1.0328 |  |  |  | Differential Pressure, Δp | 25007.6503 | Pa[A]
Expansibility Factor, Y₃ | 0.99708 | 0.01% | +-
Beta, β₃ | 0.50015
Pressure Loss | 15059.4151 | Pa[A]
[5 empty] | Differential Pressure, Δp | 25007.6503 | Pa[A]
Machined Bore (mm) | 127.2947 | mm |  |  |  | 127.2849
Operting Bore | 127.2972 | mm |  |  | Operting Bore | 127.2875 | mm
qm | 3 | kg/s |  |  | qm | 3 | kg/s

## ASME MF3CM
CALCULATION TYPE | ISO 5167:2003 |  |  | ASME MF3CM Nozzle "N4"
Convert Operating Pressure | 5000000 | Pa[A]
Convert temperature | 294.26 | °K
Calculate mass flow (if not given) | 3 | kg/s
Calc/convert density | 1.066 | kg/m³
Convert diameter with expans. | 0.25452 | m
Calc pipe area | 0.050877 | m2
Calc pipe velocity | 55.3152 | m/s
Calculate viscosity | 1.8e-05 | Pa.s
Calc Reynolds Number RaD | 833765.7062 |  |  |  | Size By Bore
Calc Reynolds Number Rad ₀ | 1674079.4597
Calc Reynolds Number Rad₁ | 1667151.5392
Calc Reynolds Number Rad₂ | 1667144.428
P2/P1 | 0.995 |  | 0.005 |  | Sizing Factor, SM | 0.25541
DP | 25000 | Pa[A] |  |  | Machined Bore | 0.12728
Downstream Pressure, P2 | 4975000 | Pa[A] |  |  | Operating Bore | 0.12729 | m
Operting Bore | 0.12729 | m |  |  | Beta, β0 | 0.50012
Machined Bore | 0.12728 | m |  |  | Calc Reynolds Number Rad ₀ | 1667144.4207
[5 empty] | Relative Uncertainty Y | 0.009904% | +-
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  |  | Co-efficient of Discharge, C | 0.99672 | 2% | +-
Sizing Factor, SM | 0.25541 |  |  |  | Initial Expansibility Factor, Y | 0.99708 | 0.009904% | +-
Initial Beta, β | 0.49804 |  |  |  | Beta, β | 0.49891
[5 empty] | E | 1.0325
Co-efficient of Discharge, C0 | 0.99161
Expansibility Factor, Y0 | 0.99708
Beta, β0 | 0.50011
Co-efficient of Discharge, C1 | 0.9916
Expansibility Factor, Y1 | 0.99708
Beta, β1 | 0.50012
Co-efficient of Discharge, C₂ | 0.9916
Expansibility Factor, Y₂ | 0.99708
Beta, β₂ | 0.50012
Relative Uncertainty Y₃ | 0.01%
Co-efficient of Discharge, C₃ | 0.9916 | 2% | +-
E | 1.0328 |  |  |  | Differential Pressure, Δp | 24760.0538 | Pa[A]
Expansibility Factor, Y₃ | 0.99708 | 0.01% | +-
Beta, β₃ | 0.50012
Pressure Loss | 15059.4156 | Pa[A]
[5 empty] | Differential Pressure, Δp | 24760.0538 | Pa[A]
Machined Bore (mm) | 127.2849 | mm |  |  |  | 127.2849
Operting Bore | 127.2875 | mm |  |  | Operting Bore | 127.2875 | mm
qm | 3 | kg/s |  |  | qm | 3.001 | kg/s

## PTC-6 Nozzle Throat Tap
CALCULATION TYPE | ISO 5167:2003 |  |  | PTC-6-Nozzle "N1"
Convert Operating Pressure | 5000000 | Pa[A]
Convert temperature | 294.26 | °K
Calculate mass flow (if not given) | 3 | kg/s
Calc/convert density | 1.066 | kg/m³
Convert diameter with expans. | 0.25452 | m
Calc pipe area | 0.050877 | m2
Calc pipe velocity | 55.3152 | m/s
Calculate viscosity | 1.8e-05 | Pa.s
Calc Reynolds Number RaD | 833765.7062 |  |  |  | Size By Bore
Calc Reynolds Number Rad ₀ | 1674079.4597
Calc Reynolds Number Rad₁ | 1671183.391
Calc Reynolds Number Rad₂ | 1671182.2738
P2/P1 | 0.995 |  | 0.005 |  | Sizing Factor, SM | 0.25541
DP | 25000 | Pa[A] |  |  | Machined Bore | 0.12728
Downstream Pressure, P2 | 4975000 | Pa[A] |  |  | Operating Bore | 0.12729 | m
Operting Bore | 0.12698 | m |  |  | Beta, β0 | 0.50012
Machined Bore | 0.12698 | m |  |  | Calc Reynolds Number Rad ₀ | 1667144.4207
[5 empty] | Calc Reynolds Number Rad | 1667144.4207
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  |  | Relative Uncertainty Y | 0.009904%
Sizing Factor, SM | 0.25541 |  |  |  | Co-efficient of Discharge, C | 0.99673 | 0.03% | +-
Initial Beta, β | 0.49804 |  |  |  | Initial Expansibility Factor, Y | 0.99708 | 0.009904% | +-
[5 empty] | Beta, β | 0.49891
[5 empty] | E | 1.0325
Co-efficient of Discharge, C0 | 0.99673
Expansibility Factor, Y0 | 0.99708
Beta, β0 | 0.49891
0.027835
Co-efficient of Discharge, C1 | 0.99673
Expansibility Factor, Y1 | 0.99708
Beta, β1 | 0.49891
Co-efficient of Discharge, C₂ | 0.99673
Expansibility Factor, Y₂ | 0.99708
Beta, β₂ | 0.49891
Relative Uncertainty Y₃ | 0.01%
Co-efficient of Discharge, C₃ | 0.99673 | 0.03% | +-
E | 1.0325
Expansibility Factor, Y₃ | 0.99708 | 0.01% | +- |  | Differential Pressure, Δp | 24759.3456 | Pa[A]
Beta, β₃ | 0.49891
Pressure Loss | 15059.433 | Pa[A]
Machined Bore (mm) | 126.9774 | mm |  |  | Differential Pressure, Δp | 24759.3456 | Pa[A]
Operting Bore | 126.9799 | mm |  |  |  | 127.2849
qm | 3 | kg/s |  |  | Operting Bore | 127.2875 | mm
[5 empty] | qm | 3.001 | kg/s

## Venturi Nozzle
CALCULATION TYPE | ISO 5167:2003 |  |  | Venturi Nozzle "N5"
Convert Operating Pressure | 5000000 | Pa[A]
Convert temperature | 294.26 | °K
Calculate mass flow (if not given) | 3 | kg/s
Calc/convert density | 1.066 | kg/m³
Convert diameter with expans. | 0.25452 | m
Calc pipe area | 0.050877 | m2
Calc pipe velocity | 55.3152 | m/s
Calculate viscosity | 1.8e-05 | Pa.s
Calc Reynolds Number | 833765.7062
Size By Bore
P2/P1 | 0.995 |  |  |  | Sizing Factor, SM | 0.25541
DP | 25000 | Pa[A] |  |  | Machined Bore | 0.12728
Downstream Pressure, P2 | 4975000 | Pa[A] |  |  | Operating Bore | 0.12729 | m
Operting Bore | 0.12818 | m |  |  | Beta, β0 | 0.50012
Machined Bore | 0.12818 | m |  |  | A | 0.027888
Uncertainty C
[5 empty] | Relative Uncertainty Y | 0.01028% | +-
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  |  | Co-efficient of Discharge, C | 0.97713 | 1.2965 | +-
Sizing Factor, SM | 0.25541 |  |  |  | Initial Expansibility Factor, Y | 0.99708 | 2.257% | +-
Initial Beta, β | 0.49804 |  |  |  | Beta, β | 0.50357
| 0.027796 |  |  |  | E | 1.0338
Co-efficient of Discharge, C0 | 0.97729
Expansibility Factor, Y0 | 0.99708
Beta, β0 | 0.50353
0.028041
Co-efficient of Discharge, C1 | 0.97686
Expansibility Factor, Y1 | 0.99707
Beta, β1 | 0.50364
0.028045
Co-efficient of Discharge, C₂ | 0.97685
Expansibility Factor, Y₂ | 0.99707
Beta, β₂ | 0.50364
Uncertainty C₃
Relative Uncertainty Y₃ | 2.257%
Co-efficient of Discharge, C₃ | 0.97685 | 1.297% | +-
E | 1.0338 |  |  |  | Differential Pressure, Δp | 25698.2192 | Pa[A]
Expansibility Factor, Y₃ | 0.99707 | 2.257% | +-
Beta, β₃ | 0.50364
Pressure Loss | 15059.369 | Pa[A]
[5 empty] | Differential Pressure, Δp | 25698.2192 | Pa[A]
Machined Bore (mm) | 128.182 | mm |  |  |  | 127.2849
Operting Bore | 128.1846 | mm |  |  | Operting Bore | 127.2875 | mm
qm | 3 | kg/s |  |  | qm | 2.9972 | kg/s