## Sheet1
Liquid | 316L Pipe | 1.789e-05 | DP | Pa[A]
Gas | CS Pipe | 1.353e-05 | Bore | m

## Input
Venturi Type Code | V1
Venturi Type | Machined Venturi | [6 empty] | Fabricated Venturi
Machined Venturi
Fluid | Gas | [6 empty] | 'As Cast' Venturi
Operating Pressure | 90000 | Pa[A]
Operating Temperature | 200 | °K
Operating Density | 1.066 | kg/m3
Compressibility | 0.999
Operating Viscosity | 1.8e-05 | Pa.s
Isentropic Index | 1.4
Flowrate | 1 | kg/s
Materials | Pipe | 1.7031e-05 |  | 1.7031e-05
| Element (Throat) | 1.185e-05 |  | 1.185e-05
Co-efficient of Discharge By Model Type | 0.995
Enter Calibrated C of E
As Calibrated Co-efficient of Discharge "OVERIDE" | 0.985 |  | FALSE | As Calibrated only : Can we hide using special functions like we do for the rules?
Pipe ID | 0.24 | m |  | 240 | mm
DP | 2000 | Pa[A] |  |  | Throat Bore | 0.083749 | m
Convert Operating Pressure | 90000 | Pa[A]
Convert temperature | 200 | °K
Calculate mass flow (if not given) | 1 | kg/s
Calc/convert density | 1.066 | kg/m³
Convert diameter with expans. | 0.23974 | m
Calc pipe area | 0.045139 | m2
Calc pipe velocity | 20.7821 | m/s
Calculate viscosity | 1.8e-05 | Pa.s
Calc Reynolds Number | 295057.0627
C of E Overid e

## Venturi ISO
CALCULATION TYPE | ISO 5167:2003 |  |  | Machined Venturi | V1
Convert Operating Pressure | 90000 | Pa[A]
Convert temperature | 200 | °K
Calculate mass flow (if not given) | 1 | kg/s | [8 empty] | Annex B ISO - 5167
Calc/convert density | 1.066 | kg/m³
Convert diameter with expans. | 0.23974 | m
Calc pipe area | 0.045139 | m2 | [7 empty] | Machined "V1" |  |  | Fabricated "V2"
Calc pipe velocity | 20.7821 | m/s |  |  | 516158.6598 |  |  |  |  | Red | C | Uncertainty(a) % | ReD | C | Uncertainty(a) %
Calculate viscosity | 1.8e-05 | Pa.s | [5 empty] | 50000 |  | 5*10^4 | 0.97 | 3 | 4*10^4 | 0.96 | 3
Calc Reynolds Number "ReD" | 295057.0627 | [6 empty] | 100000 |  | 1*10^5 | 0.977 | 2.5 | 6*10^4 | 0.97 | 2.5
Calc Reynolds Number "Red" | 516158.6598 |  |  | Size By Bore |  |  |  | 200000 |  | 2*10^5 | 0.992 | 2.5 | 1*10^5 | 0.98 | 2.5
[8 empty] | 300000 |  | 3*10^5 | 0.998 | 1.5 |  | 0.985 | 1
P2/P1 | 0.97778 |  |  | Sizing Factor, SM | 0.33926 |  |  | 500000 | 1000000 | 5*10^5 - 10^6 | 0.995 | 1
DP | 2000 | Pa[A] |  | Machined Bore | 0.083749 |  |  | 1000000 | 2000000 | 10^6 - 2*10^6 | 1 | 2
Downstream Pressure, P2 | 88000 | Pa[A] |  | Operating Bore | 0.083657 | m |  | 2000000 | 100000000 | 2*10^6 - 10^8 | 1.01 | 3
Operting Bore | 0.13704 | m |  | Beta, β0 | 0.34895
Machined Bore | 0.13719 | m |  | A | 0.048006
|  |  |  | Co-efficient of Discharge, C | 0.995 | ± | 1%
|  |  |  | Initial Expansibility Factor, Y0 | 0.98779 |  |  |  |  | 20000 | 1000000
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  | Beta, β1 | 0.57122 | ± | 0.1141% | V1 | The Discharge Coefficient C (0.995) is only valid under the following conditions - OD = 50mm - 250mm Beta = 0.4 - 0.75 ReD = 2*10^5 - 1*10^6
Sizing Factor, SM | 0.33926 |  |  | E | 1.0075 |  |  | V2 | The Discharge Coefficient C (0.985)is only valid under the following conditions - OD = 200mm - 1200mm Beta = 0.4 - 0.75 ReD = 2*10^5 - 2*10^6
Initial Beta, β | 1.5839 | [8 empty] | 200000 | 2000000
A | 0.16101
|  |  |  | Uncertainty C | 1%
Co-efficient of Discharge, C0 | 0.995 |  |  | Relative Uncertainty Y | 0.1141%
Expansibility Factor, Y0 | 1.0071
Beta, β0 | 0.56629
A | 0.070714 |  |  | Differential Pressure, Δp | 15833.1798 | Pa[A]
Co-efficient of Discharge, C1 | 0.995
Expansibility Factor, Y1 | 0.98624
Beta, β1 | 0.57162
A | 0.071247
A | 0.071249
Co-efficient of Discharge, C2 | 0.995 | ± | 1%
E | 1.0581
Expansibility Factor, Y2 | 0.98616 | ± | 0.1142%
Beta, β2 | 0.57164
Pressure Loss 15 deg cone | 274.3704 | Pa | If 15 Degree cone selected
Pressure Loss 7 deg cone | 204.1693 | pa | If 7 Degree cone selected
Uncertainty C | 1%
Relative Uncertainty Y | 0.1142%
|  |  |  | Differential Pressure, Δp | 15833.1798 | Pa[A]
Machined Bore (mm) | 137.1937 | mm |  |  | 83.7491
Operting Bore | 137.0422 | mm |  | Operting Bore | 83.6567 | mm
qm | 0.99992 | kg/s |  | qm | 1 | kg/s
Iterate until B69=B27