## Sheet1
Concentric Orifice | Corner taps - ISO 5167-2:2003 |  | Liquid |  | 316L Pipe | 1.789e-05 | DP | Pa[A]
| Flange taps - ISO 5167-2:2003 |  | Gas |  | CS Pipe | 1.353e-05 | Bore | m
D & D/2 taps - ISO 5167-2:2003
2½ & 8D taps - ISO 5167-2:2003
Conical Entrance Orifice | Corner taps - ISO 5167-2:2003
Flange taps - ISO 5167-2:2003
D & D/2 taps - ISO 5167-2:2003
2½ & 8D taps - ISO 5167-2:2003
Eccentric Orifice | Corner taps - ISO 5167-2:2003
Flange taps - ISO 5167-2:2003
D & D/2 taps - ISO 5167-2:2003
2½ & 8D taps - ISO 5167-2:2003
Quarter Circle Orifice | Corner taps - ISO 5167-2:2003
Flange taps - ISO 5167-2:2003
D & D/2 taps - ISO 5167-2:2003
2½ & 8D taps - ISO 5167-2:2003
Segmental Orifice | Corner taps - ISO 5167-2:2003
Flange taps - ISO 5167-2:2003
D & D/2 taps - ISO 5167-2:2003
2½ & 8D taps - ISO 5167-2:2003
|  | ISO 5167 | Miller | AGA-3
Concentric Orifice | Corner taps | ü | ü | û
| Flange taps | ü | ü | ü
| D & D/2 taps | ü | ü | û
| 2½ & 8D taps | û | ü | û
Conical Entrance Orifice | Corner taps | ü | ü | û
| Flange taps | û | û | û
| D & D/2 taps | û | û | û
| 2½ & 8D taps | û | û | û
Eccentric Orifice | Corner taps | ü | ü | û
| Flange taps (90° or 180°) | û | ü | û
| D & D/2 taps | û | û | û
| 2½ & 8D taps | û | û | û
Quarter Circle Orifice | Corner taps | ü* | û | û
| Flange taps | ü* | ü | û
| D & D/2 taps | û | û | û
| 2½ & 8D taps | û | û | û
Segmental Orifice | Corner taps | û | û | û
| Flange taps | û | ü | û
| D & D/2 taps | û | û | û
| 2½ & 8D taps | û | û | û
* Same equation for corner and flange taps

## Input
Fluid | Gas
Operating Pressure | 201325 | Pa[A]
Operating Temperature | 273.15 | °K
Operating Density | 0.5 | kg/m3
Compressibility | 1
Operating Viscosity | 0.001 | Pa.s
Isentropic Index | 1.5
Liquid Vapour Pressure |  | Pa[A]
Flowrate (x4) | 3 | kg/s
Materials | CS Pipe | 1.353e-05
Co-efficient of Expansion | 316L Element | 1.789e-05
Pipe ID | 0.54768 | m
Pipe WT | 0.00602 | m
DP | 50000 | Pa[A] | Bore | 0.16073 | m
Convert Operating Pressure | 201325 | Pa[A]
Convert temperature | 273.15 | °K
Calculate mass flow (if not given) | 3 | kg/s
Calc/convert density | 0.5 | kg/m³
Convert diameter with expans. | 0.54753 | m
Calc pipe area | 0.23546 | m2
Calc pipe velocity | 25.4825 | m/s
Calculate viscosity | 0.001 | Pa.s
Calc Reynolds Number | 6976.2499

## Concentric - Corner
CALCULATION TYPE | ISO 5167:2003 |  |  | CH/FPD/ORIFICE/DESIGN | C1 | Concentric - Corner taps
Convert Operating Pressure | 201325 | Pa[A]
Convert temperature | 273.15 | °K
Calculate mass flow (if not given) | 3 | kg/s
Calc/convert density | 0.5 | kg/m³
Convert diameter with expans. | 0.54753 | m
Calc pipe area | 0.23546 | m2
Calc pipe velocity | 25.4825 | m/s
Calculate viscosity | 0.001 | Pa.s
Calc Reynolds Number | 6976.2499
DP | 50000 | Pa[A] |  | Operating Bore | 0.16067 | m
Downstream Pressure, P2 | 151325 | Pa[A] |  | Beta | 0.29345
L1 | 0 |  |  | L1 | 0
L'2 | 0 |  |  | L'2 | 0
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  | A | 0.83586
Sizing Factor, SM | 0.056981 |  |  | M'2 | 0
Initial Beta, β0 | 0.29914 |  |  | Co-efficient of Discharge, C | 0.60693
A0 | 0.84881 |  |  | Initial Expansibility Factor, Y0 | 1
M'2,0 | 0 |  |  | Differential Pressure, Δp | 58990.2533 | Pa[A]
Co-efficient of Discharge, C0 | 0.60722 |  |  | Expansibility Factor, Y | 0.92716
Expansibility Factor, Y0 | 0.9388 |  |  | Differential Pressure, Δp | 68623.8021 | Pa[A]
Beta, β1 | 0.31537 |  |  | Expansibility Factor, Y | 0.91437
A1 | 0.88545
M'2,1 | 0
Co-efficient of Discharge, C1 | 0.60809
Expansibility Factor, Y1 | 0.93871
Operting Bore | 0.17268 | m
Machined Bore | 0.17274 | m
Machined Bore (mm) | 172.7379 | mm |  | Differential Pressure, Δp | 70556.3817 | Pa[A]
qm | 2.9997 | kg/s |  | qm | 3 | kg/s
Iterate until B57=B27
Device
| Corner Taps | Flange Taps | D and D/2 Taps | Units | Warning
Min bore,d | 12.5 | 12.5 | 12.5 | mm | Bore too low
Min pipe ID, D | 50 | 50 | 50 | mm | Pipe ID too low
Max pipe ID, D | 1000 | 1000 | 1000 | mm | Pipe ID too high
Min beta, β | 0.1 | 0.1 | 0.1 |  | Beta ratio too low
Max beta, β | 0.75 | 0.75 | 0.75 |  | Beta ratio too high
Min Reynolds | 5000 | 5000 AND 170β2D | 5000 | For Beta less than 0.56 | Reynolds Number too low
Min Reynolds | 16000β2 | 5000 AND 170β2D | 16000β2 | For Beta more than 0.56 | Reynolds Number too low
Max p2/p1 | 0.75 | 0.75 | 0.75 |  | Pressure drop too high
Note on A40: Jen Wilson: Miller Table 9.15

## Concentric - Flange
CALCULATION TYPE | ISO 5167:2003 |  |  | CH/FPD/ORIFICE/DESIGN | C2 | Concentric - Flange taps
Convert Operating Pressure | 201325 | Pa[A]
Convert temperature | 273.15 | °K
Calculate mass flow (if not given) | 3 | kg/s
Calc/convert density | 0.5 | kg/m³
Convert diameter with expans. | 0.54753 | m
Calc pipe area | 0.23546 | m2
Calc pipe velocity | 25.4825 | m/s
Calculate viscosity | 0.001 | Pa.s
Calc Reynolds Number | 6976.2499
DP | 50000 | Pa[A] |  | Operating Bore | 0.16067 | m
Downstream Pressure, P2 | 151325 | Pa[A] |  | Beta | 0.29345
L1 | 0.04639 |  |  | L1 | 0.04639
L'2 | 0.04639 |  |  | L'2 | 0.04639
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  | A | 0.83586
Sizing Factor, SM | 0.056981 |  |  | M'2 | 0.13131
Initial Beta, β0 | 0.29914 |  |  | Co-efficient of Discharge, C | 0.60668
A0 | 0.84881 |  |  | Initial Expansibility Factor, Y0 | 1
M'2,0 | 0.13238 |  |  | Differential Pressure, Δp | 59040.244 | Pa[A]
Co-efficient of Discharge, C0 | 0.60696 |  |  | Expansibility Factor, Y | 0.92709
Expansibility Factor, Y0 | 0.9388 |  |  | Differential Pressure, Δp | 68691.6751 | Pa[A]
Beta, β1 | 0.31544 |  |  | Expansibility Factor, Y | 0.91428
A1 | 0.8856
M'2,1 | 0.13553
Co-efficient of Discharge, C1 | 0.60781
Expansibility Factor, Y1 | 0.93871
Operting Bore | 0.17271 | m
Machined Bore | 0.17278 | m
Machined Bore (mm) | 172.775 | mm |  | Differential Pressure, Δp | 68691.6751 | Pa[A]
qm | 2.9997 | kg/s |  | qm | 3 | kg/s
Iterate until B57=B27
Device
| Corner Taps | Flange Taps | D and D/2 Taps | Units | Warning
Min bore,d | 12.5 | 12.5 | 12.5 | mm | Bore too low
Min pipe ID, D | 50 | 50 | 50 | mm | Pipe ID too low
Max pipe ID, D | 1000 | 1000 | 1000 | mm | Pipe ID too high
Min beta, β | 0.1 | 0.1 | 0.1 |  | Beta ratio too low
Max beta, β | 0.75 | 0.75 | 0.75 |  | Beta ratio too high
Min Reynolds | 5000 | 5000 AND 170β2D | 5000 | For Beta less than 0.56 | Reynolds Number too low
Min Reynolds | 16000β2 | 5000 AND 170β2D | 16000β2 | For Beta more than 0.56 | Reynolds Number too low
Max p2/p1 | 0.75 | 0.75 | 0.75 |  | Pressure drop too high
Note on A40: Jen Wilson: Miller Table 9.15

## Concentric - D D2
CALCULATION TYPE | ISO 5167:2003 |  |  | CH/FPD/ORIFICE/DESIGN | C3 | Concentric - D & D/2 taps
Convert Operating Pressure | 201325 | Pa[A]
Convert temperature | 273.15 | °K
Calculate mass flow (if not given) | 3 | kg/s
Calc/convert density | 0.5 | kg/m³
Convert diameter with expans. | 0.54753 | m
Calc pipe area | 0.23546 | m2
Calc pipe velocity | 25.4825 | m/s
Calculate viscosity | 0.001 | Pa.s
Calc Reynolds Number | 6976.2499
DP | 50000 | Pa[A] |  | Operating Bore | 0.16067 | m
Downstream Pressure, P2 | 151325 | Pa[A] |  | Beta | 0.29345
L1 | 1 |  |  | L1 | 1
L'2 | 0.47 |  |  | L'2 | 0.47
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  | A | 0.83586
Sizing Factor, SM | 0.056981 |  |  | M'2 | 1.3304
Initial Beta, β0 | 0.29914 |  |  | Co-efficient of Discharge, C | 0.60574
A0 | 0.84881 |  |  | Initial Expansibility Factor, Y0 | 1
M'2,0 | 1.3412 |  |  | Differential Pressure, Δp | 59222.3588 | Pa[A]
Co-efficient of Discharge, C0 | 0.60601 |  |  | Expansibility Factor, Y | 0.92685
Expansibility Factor, Y0 | 0.9388 |  |  | Differential Pressure, Δp | 68939.1012 | Pa[A]
Beta, β1 | 0.31568 |  |  | Expansibility Factor, Y | 0.91395
A1 | 0.88615
M'2,1 | 1.3736
Co-efficient of Discharge, C1 | 0.60684
Expansibility Factor, Y1 | 0.93871
Operting Bore | 0.17285 | m
Machined Bore | 0.17291 | m
Machined Bore (mm) | 172.9088 | mm |  | Differential Pressure, Δp | 68939.1012 | Pa[A]
qm | 2.9997 | kg/s |  | qm | 3 | kg/s
Iterate until B57=B27
Device
| Corner Taps | Flange Taps | D and D/2 Taps | Units | Warning
Min bore,d | 12.5 | 12.5 | 12.5 | mm | Bore too low
Min pipe ID, D | 50 | 50 | 50 | mm | Pipe ID too low
Max pipe ID, D | 1000 | 1000 | 1000 | mm | Pipe ID too high
Min beta, β | 0.1 | 0.1 | 0.1 |  | Beta ratio too low
Max beta, β | 0.75 | 0.75 | 0.75 |  | Beta ratio too high
Min Reynolds | 5000 | 5000 AND 170β2D | 5000 | For Beta less than 0.56 | Reynolds Number too low
Min Reynolds | 16000β2 | 5000 AND 170β2D | 16000β2 | For Beta more than 0.56 | Reynolds Number too low
Max p2/p1 | 0.75 | 0.75 | 0.75 |  | Pressure drop too high
Note on A40: Jen Wilson: Miller Table 9.15

## Quarter Circle
CALCULATION TYPE | ISO 5167:2003 |  |  | CH/FPD/ORIFICE/DESIGN | Q1 | Quarter circle - Corner taps
[5 empty] | Q2 | Quarter circle - Flange taps
Convert Operating Pressure | 201325 | Pa[A]
Convert temperature | 273.15 | °K
Calculate mass flow (if not given) | 3 | kg/s
Calc/convert density | 0.5 | kg/m³
Convert diameter with expans. | 0.54753 | m
Calc pipe area | 0.23546 | m2
Calc pipe velocity | 25.4825 | m/s
Calculate viscosity | 0.001 | Pa.s
Calc Reynolds Number | 6976.2499
DP | 50000 | Pa[A] |  | Operating Bore | 0.16067 | m
Downstream Pressure, P2 | 151325 | Pa[A] |  | Beta | 0.29345
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  | Co-efficient of Discharge, C | 0.77343
Sizing Factor, SM | 0.056981 |  |  | Initial Expansibility Factor, Y0 | 1
Initial Beta, β0 | 0.27082 |  |  | Differential Pressure, Δp | 36326.4392 | Pa[A]
Co-efficient of Discharge, C0 | 0.77262 |  |  | Expansibility Factor, Y | 0.95615
Expansibility Factor, Y0 | 0.93892
Beta, β1 | 0.27983
Operting Bore | 0.15322 | m
Machined Bore | 0.15327 | m
Machined Bore (mm) | 153.2722 | mm |  | Differential Pressure, Δp | 39734.6238 | Pa[A]
Iterate until B55=B27
qm | 3 | kg/s |  | qm | 3 | kg/s
Device
| Corner Taps | Units | Warning
Min bore,d | 15 | mm | Bore too low
Min pipe ID, D | - | mm | Pipe ID too low
Max pipe ID, D | 500 | mm | Pipe ID too high
Min beta, β | 0.245 |  | Beta ratio too low
Max beta, β | 0.6 |  | Beta ratio too high
Min Reynolds | 1000β +9.4x106(β-0.24)8 |  | Reynolds Number too low
Max Reynolds | 105β |  | Reynolds Number too high
Max p2/p1 | 0.75 |  | Pressure drop too high
Note on A38: Jen Wilson: Miller Table 9.15

## Eccentric
CALCULATION TYPE | ISO 5167:2003 |  |  | CH/FPD/ORIFICE/DESIGN | E1 | Eccentric - Corner taps
Convert Operating Pressure | 201325 | Pa[A]
Convert temperature | 273.15 | °K
Calculate mass flow (if not given) | 3 | kg/s
Calc/convert density | 0.5 | kg/m³
Convert diameter with expans. | 0.54753 | m
Calc pipe area | 0.23546 | m2
Calc pipe velocity | 25.4825 | m/s
Calculate viscosity | 0.001 | Pa.s
Calc Reynolds Number | 6976.2499
DP | 50000 | Pa[A] |  | Operating Bore | 0.16067 | m
Downstream Pressure, P2 | 151325 | Pa[A] |  | Beta | 0.29345
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  | Co-efficient of Discharge, C | 0.65646
Sizing Factor, SM | 0.056981 |  |  | Initial Expansibility Factor, Y0 | 1
Initial Beta, β0 | 0.30447 |  |  | Differential Pressure, Δp | 50425.3265 | Pa[A]
Co-efficient of Discharge, C0 | 0.65258 |  |  | Expansibility Factor, Y | 0.93828
Expansibility Factor, Y0 | 0.93877 |  |  | Differential Pressure, Δp | 57277.1162 | Pa[A]
Beta, β1 | 0.30432 |  |  | Expansibility Factor, Y | 0.9294
Operting Bore | 0.16663 | m
Machined Bore | 0.16668 | m
Machined Bore (mm) | 166.6848 | mm |  | Differential Pressure, Δp | 58377.3515 | Pa[A]
Iterate until B55=B27
qm | 3 | kg/s |  | qm | 3.0287 | kg/s
Device
| Corner Taps | Units | Warning
Min bore,d | 50 | mm | Bore too low
Min pipe ID, D | 100 | mm | Pipe ID too low
Max pipe ID, D | 1000 | mm | Pipe ID too high
Min beta, β | 0.46 |  | Beta ratio too low
Max beta, β | 0.84 |  | Beta ratio too high
Min Reynolds | 18522.1857 |  | Reynolds Number too low
Max Reynolds | 304320.4376 |  | Reynolds Number too high
Max p2/p1 | 0.75 |  | Pressure drop too high
Note on A38: Jen Wilson: Miller Table 9.15

## Conical
CALCULATION TYPE | ISO 5167:2003 |  |  | CH/FPD/ORIFICE/DESIGN | L1 | Conical entrance - Corner taps
Convert Operating Pressure | 201325 | Pa[A]
Convert temperature | 273.15 | °K
Calculate mass flow (if not given) | 3 | kg/s
Calc/convert density | 0.5 | kg/m³
Convert diameter with expans. | 0.54753 | m
Calc pipe area | 0.23546 | m2
Calc pipe velocity | 25.4825 | m/s
Calculate viscosity | 0.001 | Pa.s
Calc Reynolds Number | 6976.2499
DP | 50000 | Pa[A] |  | Operating Bore | 0.16067 | m
Downstream Pressure, P2 | 151325 | Pa[A] |  | Beta | 0.29345
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  | Co-efficient of Discharge, C | 0.734
Sizing Factor, SM | 0.056981 |  |  | Initial Expansibility Factor, Y0 | 1
Initial Beta, β0 | 0.2782 |  |  | Differential Pressure, Δp | 40334.0747 | Pa[A]
Co-efficient of Discharge, C0 | 0.734 |  |  | Pressure ratio, τ1 | 0.79966 | Pa[A]
Pressure ratio, τ | 0.75165 |  |  | Concentric Expansibility Factor, Y | 0.93026
Concentric Expansibility Factor, Y | 0.9389 | 0.93883 |  | ISA 1932 Nozzle Expansibility Factor, Y | 0.89255
ISA 1932 Nozzle Expansibility Factor, Y | 0.86484 | 0.86465 |  | Expansibility Factor, Y | 0.9114
Expansibility Factor, Y | 0.90187 | 0.90174
Beta, β1 | 0.29285 | 0.29287
Operting Bore | 0.16034 | 0.16035
Machined Bore | 0.1604 | 0.16041
Machined Bore (mm) | 160.401 | mm |  | Differential Pressure, Δp | 48556.8966 | Pa[A]
qm | 3 | kg/s |  | qm | 3 | kg/s
Iterate until B45=B27
Device
|  | Units | Warning
Min bore,d | 6 | mm | Bore too low
Min pipe ID, D | 50 | mm | Pipe ID too low
Max pipe ID, D | 500 | mm | Pipe ID too high
Min beta, β | 0.1 |  | Beta ratio too low
Max beta, β | 0.316 |  | Beta ratio too high
Min Reynolds | 80 |  | Reynolds Number too low
Max Reynolds | 2*105*beta |  | Reynolds Number too high
Max p2/p1 | 0.75 |  | Pressure drop too high
Note on A38: Jen Wilson: Miller Table 9.15