## Sheet1
Concentric Orifice | Corner taps - ISO 5167-2:2003 |  | Liquid |  | 316L Pipe | 1.789e-05 | DP | Pa[A]
| Flange taps - ISO 5167-2:2003 |  | Gas |  | CS Pipe | 1.353e-05 | Bore | m
D & D/2 taps - ISO 5167-2:2003
2½ & 8D taps - ISO 5167-2:2003
Conical Entrance Orifice | Corner taps - ISO 5167-2:2003
Flange taps - ISO 5167-2:2003
D & D/2 taps - ISO 5167-2:2003
2½ & 8D taps - ISO 5167-2:2003
Eccentric Orifice | Corner taps - ISO 5167-2:2003
Flange taps - ISO 5167-2:2003
D & D/2 taps - ISO 5167-2:2003
2½ & 8D taps - ISO 5167-2:2003
Quarter Circle Orifice | Corner taps - ISO 5167-2:2003
Flange taps - ISO 5167-2:2003
D & D/2 taps - ISO 5167-2:2003
2½ & 8D taps - ISO 5167-2:2003
Segmental Orifice | Corner taps - ISO 5167-2:2003
Flange taps - ISO 5167-2:2003
D & D/2 taps - ISO 5167-2:2003
2½ & 8D taps - ISO 5167-2:2003
|  | ISO 5167 | Miller | AGA-3
Concentric Orifice | Corner taps | ü | ü | û
| Flange taps | ü | ü | ü
| D & D/2 taps | ü | ü | û
| 2½ & 8D taps | û | ü | û
Conical Entrance Orifice | Corner taps | ü | ü | û
| Flange taps | û | û | û
| D & D/2 taps | û | û | û
| 2½ & 8D taps | û | û | û
Eccentric Orifice | Corner taps | ü | ü | û
| Flange taps (90° or 180°) | û | ü | û
| D & D/2 taps | û | û | û
| 2½ & 8D taps | û | û | û
Quarter Circle Orifice | Corner taps | ü* | û | û
| Flange taps | ü* | ü | û
| D & D/2 taps | û | û | û
| 2½ & 8D taps | û | û | û
Segmental Orifice | Corner taps | û | û | û
| Flange taps | û | ü | û
| D & D/2 taps | û | û | û
| 2½ & 8D taps | û | û | û
* Same equation for corner and flange taps

## Input
Fluid | Gas
Operating Pressure | 351325 | Pa[A]
Operating Temperature | 418.15 | °K
Operating Density | 1.9142 | kg/m3
Compressibility | 1.9142
Operating Viscosity | 1.383e-05 | Pa.s
Isentropic Index | 1.308
Liquid Vapour Pressure |  | Pa[A]
Flowrate (x4) | 6 | kg/s
Materials | CS Pipe | 1.185e-05
Co-efficient of Expansion | 316L Element | 1.7031e-05
Pipe ID | 0.3396 | m
Pipe WT | 0.008 | m
DP | 25000 | Pa[A] | Bore | 0.19776 | m
Convert Operating Pressure | 351325 | Pa[A]
Convert temperature | 418.15 | °K
Calculate mass flow (if not given) | 6 | kg/s
Calc/convert density | 1.9142 | kg/m³
Convert diameter with expans. | 0.3401 | m
Calc pipe area | 0.090847 | m2
Calc pipe velocity | 34.5027 | m/s
Calculate viscosity | 1.383e-05 | Pa.s
Calc Reynolds Number | 1624159.57

## Concentric - Corner
CALCULATION TYPE | ISO 5167:2003 |  |  | CH/FPD/ORIFICE/DESIGN | C1 | Concentric - Corner taps
Convert Operating Pressure | 351325 | Pa[A]
Convert temperature | 418.15 | °K
Calculate mass flow (if not given) | 6 | kg/s
Calc/convert density | 1.9142 | kg/m³
Convert diameter with expans. | 0.3401 | m
Calc pipe area | 0.090847 | m2
Calc pipe velocity | 34.5027 | m/s
Calculate viscosity | 1.383e-05 | Pa.s
Calc Reynolds Number | 1624159.57
DP | 25000 | Pa[A] |  | Operating Bore | 0.19818 | m
Downstream Pressure, P2 | 326325 | Pa[A] |  | Beta | 0.58271
L1 | 0 |  |  | L1 | 0
L'2 | 0 |  |  | L'2 | 0
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  | A | 0.018487
Sizing Factor, SM | 0.21348 |  |  | M'2 | 0
Initial Beta, β0 | 0.57898 |  |  | Co-efficient of Discharge, C | 0.60482
A0 | 0.018392 |  |  | Initial Expansibility Factor, Y0 | 1
M'2,0 | 0 |  |  | Differential Pressure, Δp | 23899.6052 | Pa[A]
Co-efficient of Discharge, C0 | 0.60479 |  |  | Expansibility Factor, Y | 0.9794
Expansibility Factor, Y0 | 0.97852 |  |  | Differential Pressure, Δp | 24915.6283 | Pa[A]
Beta, β1 | 0.58252 |  |  | Expansibility Factor, Y | 0.97852
A1 | 0.018482
M'2,1 | 0
Co-efficient of Discharge, C1 | 0.60481
Expansibility Factor, Y1 | 0.97845
Operting Bore | 0.19812 | m
Machined Bore | 0.1977 | m
Machined Bore (mm) | 197.6966 | mm |  | Differential Pressure, Δp | 24960.6415 | Pa[A]
qm | 5.9996 | kg/s |  | qm | 6 | kg/s
Iterate until B57=B27
Device
| Corner Taps | Flange Taps | D and D/2 Taps | Units | Warning
Min bore,d | 12.5 | 12.5 | 12.5 | mm | Bore too low
Min pipe ID, D | 50 | 50 | 50 | mm | Pipe ID too low
Max pipe ID, D | 1000 | 1000 | 1000 | mm | Pipe ID too high
Min beta, β | 0.1 | 0.1 | 0.1 |  | Beta ratio too low
Max beta, β | 0.75 | 0.75 | 0.75 |  | Beta ratio too high
Min Reynolds | 5000 | 5000 AND 170β2D | 5000 | For Beta less than 0.56 | Reynolds Number too low
Min Reynolds | 16000β2 | 5000 AND 170β2D | 16000β2 | For Beta more than 0.56 | Reynolds Number too low
Max p2/p1 | 0.75 | 0.75 | 0.75 |  | Pressure drop too high
Note on A40: Jen Wilson: Miller Table 9.15

## Concentric - Flange
CALCULATION TYPE | ISO 5167:2003 |  |  | CH/FPD/ORIFICE/DESIGN | C2 | Concentric - Flange taps
Convert Operating Pressure | 351325 | Pa[A]
Convert temperature | 418.15 | °K
Calculate mass flow (if not given) | 6 | kg/s
Calc/convert density | 1.9142 | kg/m³
Convert diameter with expans. | 0.3401 | m
Calc pipe area | 0.090847 | m2
Calc pipe velocity | 34.5027 | m/s
Calculate viscosity | 1.383e-05 | Pa.s
Calc Reynolds Number | 1624159.57
DP | 25000 | Pa[A] |  | Operating Bore | 0.19818 | m
Downstream Pressure, P2 | 326325 | Pa[A] |  | Beta | 0.58271
L1 | 0.074683 |  |  | L1 | 0.074683
L'2 | 0.074683 |  |  | L'2 | 0.074683
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  | A | 0.018487
Sizing Factor, SM | 0.21348 |  |  | M'2 | 0.35795
Initial Beta, β0 | 0.57898 |  |  | Co-efficient of Discharge, C | 0.60432
A0 | 0.018392 |  |  | Initial Expansibility Factor, Y0 | 1
M'2,0 | 0.35477 |  |  | Differential Pressure, Δp | 23938.4233 | Pa[A]
Co-efficient of Discharge, C0 | 0.60429 |  |  | Expansibility Factor, Y | 0.97936
Expansibility Factor, Y0 | 0.97852 |  |  | Differential Pressure, Δp | 24957.8163 | Pa[A]
Beta, β1 | 0.58273 |  |  | Expansibility Factor, Y | 0.97848
A1 | 0.018487 |  |  | DP3 | 25003.0584
M'2,1 | 0.35796 |  |  | Y4 | 0.97844
Co-efficient of Discharge, C1 | 0.60433 |  |  | DP4 | 25005.0699
Expansibility Factor, Y1 | 0.97844 |  |  | Y5 | 0.97844
|  |  |  | DP5 | 25005.1593
Operting Bore | 0.19819 | m |  | Y6 | 0.97844
Machined Bore | 0.19777 | m
Machined Bore (mm) | 197.7686 | mm |  | Differential Pressure, Δp | 25005.1633 | Pa[A]
qm | 5.9995 | kg/s |  | qm | 6.0057 | kg/s
Iterate until B57=B27
Device
| Corner Taps | Flange Taps | D and D/2 Taps | Units | Warning
Min bore,d | 12.5 | 12.5 | 12.5 | mm | Bore too low
Min pipe ID, D | 50 | 50 | 50 | mm | Pipe ID too low
Max pipe ID, D | 1000 | 1000 | 1000 | mm | Pipe ID too high
Min beta, β | 0.1 | 0.1 | 0.1 |  | Beta ratio too low
Max beta, β | 0.75 | 0.75 | 0.75 |  | Beta ratio too high
Min Reynolds | 5000 | 5000 AND 170β2D | 5000 | For Beta less than 0.56 | Reynolds Number too low
Min Reynolds | 16000β2 | 5000 AND 170β2D | 16000β2 | For Beta more than 0.56 | Reynolds Number too low
Max p2/p1 | 0.75 | 0.75 | 0.75 |  | Pressure drop too high
Note on A40: Jen Wilson: Miller Table 9.15

## Concentric - D D2
CALCULATION TYPE | ISO 5167:2003 |  |  | CH/FPD/ORIFICE/DESIGN | C3 | Concentric - D & D/2 taps
Convert Operating Pressure | 351325 | Pa[A]
Convert temperature | 418.15 | °K
Calculate mass flow (if not given) | 6 | kg/s
Calc/convert density | 1.9142 | kg/m³
Convert diameter with expans. | 0.3401 | m
Calc pipe area | 0.090847 | m2
Calc pipe velocity | 34.5027 | m/s
Calculate viscosity | 1.383e-05 | Pa.s
Calc Reynolds Number | 1624159.57
DP | 25000 | Pa[A] |  | Operating Bore | 0.19818 | m
Downstream Pressure, P2 | 326325 | Pa[A] |  | Beta | 0.58271
L1 | 1 |  |  | L1 | 1
L'2 | 0.47 |  |  | L'2 | 0.47
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  | A | 0.018487
Sizing Factor, SM | 0.21348 |  |  | M'2 | 2.2527
Initial Beta, β0 | 0.57898 |  |  | Co-efficient of Discharge, C | 0.60581
A0 | 0.018392 |  |  | Initial Expansibility Factor, Y0 | 1
M'2,0 | 2.2327 |  |  | Differential Pressure, Δp | 23820.8167 | Pa[A]
Co-efficient of Discharge, C0 | 0.60568 |  |  | Expansibility Factor, Y | 0.97947
Expansibility Factor, Y0 | 0.97852 |  |  | Differential Pressure, Δp | 24830.0176 | Pa[A]
Beta, β1 | 0.58214 |  |  | Expansibility Factor, Y | 0.97859
A1 | 0.018472
M'2,1 | 2.2496
Co-efficient of Discharge, C1 | 0.60579
Expansibility Factor, Y1 | 0.97845
Operting Bore | 0.19799 | m
Machined Bore | 0.19757 | m
Machined Bore (mm) | 197.5677 | mm |  | Differential Pressure, Δp | 24830.0176 | Pa[A]
qm | 5.9996 | kg/s |  | qm | 6 | kg/s
Iterate until B57=B27
Device
| Corner Taps | Flange Taps | D and D/2 Taps | Units | Warning
Min bore,d | 12.5 | 12.5 | 12.5 | mm | Bore too low
Min pipe ID, D | 50 | 50 | 50 | mm | Pipe ID too low
Max pipe ID, D | 1000 | 1000 | 1000 | mm | Pipe ID too high
Min beta, β | 0.1 | 0.1 | 0.1 |  | Beta ratio too low
Max beta, β | 0.75 | 0.75 | 0.75 |  | Beta ratio too high
Min Reynolds | 5000 | 5000 AND 170β2D | 5000 | For Beta less than 0.56 | Reynolds Number too low
Min Reynolds | 16000β2 | 5000 AND 170β2D | 16000β2 | For Beta more than 0.56 | Reynolds Number too low
Max p2/p1 | 0.75 | 0.75 | 0.75 |  | Pressure drop too high
Note on A40: Jen Wilson: Miller Table 9.15

## Quarter Circle
CALCULATION TYPE | ISO 5167:2003 |  |  | CH/FPD/ORIFICE/DESIGN | Q1 | Quarter circle - Corner taps
[5 empty] | Q2 | Quarter circle - Flange taps
Convert Operating Pressure | 351325 | Pa[A]
Convert temperature | 418.15 | °K
Calculate mass flow (if not given) | 6 | kg/s
Calc/convert density | 1.9142 | kg/m³
Convert diameter with expans. | 0.3401 | m
Calc pipe area | 0.090847 | m2
Calc pipe velocity | 34.5027 | m/s
Calculate viscosity | 1.383e-05 | Pa.s
Calc Reynolds Number | 1624159.57
DP | 25000 | Pa[A] |  | Operating Bore | 0.19818 | m
Downstream Pressure, P2 | 326325 | Pa[A] |  | Beta | 0.58271
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  | Co-efficient of Discharge, C | 0.83511
Sizing Factor, SM | 0.21348 |  |  | Initial Expansibility Factor, Y0 | 1
Initial Beta, β0 | 0.50324 |  |  | Differential Pressure, Δp | 12535.5868 | Pa[A]
Co-efficient of Discharge, C0 | 0.80284 |  |  | Expansibility Factor, Y | 0.98924
Expansibility Factor, Y0 | 0.97963
Beta, β1 | 0.51182
Operting Bore | 0.17407 | m
Machined Bore | 0.1737 | m
Machined Bore (mm) | 173.7017 | mm |  | Differential Pressure, Δp | 12809.8489 | Pa[A]
Iterate until B55=B27
qm | 6 | kg/s |  | qm | 6 | kg/s
Device
| Corner Taps | Units | Warning
Min bore,d | 15 | mm | Bore too low
Min pipe ID, D | - | mm | Pipe ID too low
Max pipe ID, D | 500 | mm | Pipe ID too high
Min beta, β | 0.245 |  | Beta ratio too low
Max beta, β | 0.6 |  | Beta ratio too high
Min Reynolds | 1000β +9.4x106(β-0.24)8 |  | Reynolds Number too low
Max Reynolds | 105β |  | Reynolds Number too high
Max p2/p1 | 0.75 |  | Pressure drop too high
Note on A38: Jen Wilson: Miller Table 9.15

## Eccentric
CALCULATION TYPE | ISO 5167:2003 |  |  | CH/FPD/ORIFICE/DESIGN | E1 | Eccentric - Corner taps
Convert Operating Pressure | 351325 | Pa[A]
Convert temperature | 418.15 | °K
Calculate mass flow (if not given) | 6 | kg/s
Calc/convert density | 1.9142 | kg/m³
Convert diameter with expans. | 0.3401 | m
Calc pipe area | 0.090847 | m2
Calc pipe velocity | 34.5027 | m/s
Calculate viscosity | 1.383e-05 | Pa.s
Calc Reynolds Number | 1624159.57
DP | 25000 | Pa[A] |  | Operating Bore | 0.19818 | m
Downstream Pressure, P2 | 326325 | Pa[A] |  | Beta | 0.58271
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  | Co-efficient of Discharge, C | 0.62862
Sizing Factor, SM | 0.21348 |  |  | Initial Expansibility Factor, Y0 | 1
Initial Beta, β0 | 0.56822 |  |  | Differential Pressure, Δp | 22124.0365 | Pa[A]
Co-efficient of Discharge, C0 | 0.62824 |  |  | Expansibility Factor, Y | 0.98094
Expansibility Factor, Y0 | 0.97872 |  |  | Differential Pressure, Δp | 22992.0995 | Pa[A]
Beta, β1 | 0.5727 |  |  | Expansibility Factor, Y | 0.98019
Operting Bore | 0.19478 | m
Machined Bore | 0.19436 | m
Machined Bore (mm) | 194.3648 | mm |  | Differential Pressure, Δp | 23027.4786 | Pa[A]
Iterate until B55=B27
qm | 6 | kg/s |  | qm | 6.0046 | kg/s
Device
| Corner Taps | Units | Warning
Min bore,d | 50 | mm | Bore too low
Min pipe ID, D | 100 | mm | Pipe ID too low
Max pipe ID, D | 1000 | mm | Pipe ID too high
Min beta, β | 0.46 |  | Beta ratio too low
Max beta, β | 0.84 |  | Beta ratio too high
Min Reynolds | 65598.1211 |  | Reynolds Number too low
Max Reynolds | 572704.6409 |  | Reynolds Number too high
Max p2/p1 | 0.75 |  | Pressure drop too high
Note on A38: Jen Wilson: Miller Table 9.15

## Conical
CALCULATION TYPE | ISO 5167:2003 |  |  | CH/FPD/ORIFICE/DESIGN | L1 | Conical entrance - Corner taps
Convert Operating Pressure | 351325 | Pa[A]
Convert temperature | 418.15 | °K
Calculate mass flow (if not given) | 6 | kg/s
Calc/convert density | 1.9142 | kg/m³
Convert diameter with expans. | 0.3401 | m
Calc pipe area | 0.090847 | m2
Calc pipe velocity | 34.5027 | m/s
Calculate viscosity | 1.383e-05 | Pa.s
Calc Reynolds Number | 1624159.57
DP | 25000 | Pa[A] |  | Operating Bore | 0.19818 | m
Downstream Pressure, P2 | 326325 | Pa[A] |  | Beta | 0.58271
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  | Co-efficient of Discharge, C | 0.734
Sizing Factor, SM | 0.21348 |  |  | Initial Expansibility Factor, Y0 | 1
Initial Beta, β0 | 0.52846 |  |  | Differential Pressure, Δp | 16227.2305 | Pa[A]
Co-efficient of Discharge, C0 | 0.734 |  |  | Pressure ratio, τ1 | 0.95381 | Pa[A]
Pressure ratio, τ | 0.92884 |  |  | Concentric Expansibility Factor, Y | 0.98212
Concentric Expansibility Factor, Y | 0.97933 | 0.97922 |  | ISA 1932 Nozzle Expansibility Factor, Y | 0.96881
ISA 1932 Nozzle Expansibility Factor, Y | 0.95416 | 0.95386 |  | Expansibility Factor, Y | 0.97546
Expansibility Factor, Y | 0.96674 | 0.96654
Beta, β1 | 0.53675 | 0.5368
Operting Bore | 0.18255 | 0.18257
Machined Bore | 0.18216 | 0.18218
Machined Bore (mm) | 182.1613 | mm |  | Differential Pressure, Δp | 17053.8241 | Pa[A]
qm | 6 | kg/s |  | qm | 6 | kg/s
Iterate until B45=B27
Device
|  | Units | Warning
Min bore,d | 6 | mm | Bore too low
Min pipe ID, D | 50 | mm | Pipe ID too low
Max pipe ID, D | 500 | mm | Pipe ID too high
Min beta, β | 0.1 |  | Beta ratio too low
Max beta, β | 0.316 |  | Beta ratio too high
Min Reynolds | 80 |  | Reynolds Number too low
Max Reynolds | 2*105*beta |  | Reynolds Number too high
Max p2/p1 | 0.75 |  | Pressure drop too high
Note on A38: Jen Wilson: Miller Table 9.15