## Sheet1
Concentric Orifice | Corner taps - Miller 3rd Edition | Liquid | 316L Pipe | 1.789e-05 | DP | Pa[A]
| Flange taps - Miller 3rd Edition | Gas | CS Pipe | 1.353e-05 | Bore | m
D & D/2 taps - Miller 3rd Edition
2½ & 8D taps - Miller 3rd Edition
Conical Entrance Orifice | Corner taps - Miller 3rd Edition
Flange taps - Miller 3rd Edition
D & D/2 taps - Miller 3rd Edition
2½ & 8D taps - Miller 3rd Edition
Eccentric Orifice | Corner taps - Miller 3rd Edition
Flange taps - Miller 3rd Edition
D & D/2 taps - Miller 3rd Edition
2½ & 8D taps - Miller 3rd Edition
Quarter Circle Orifice | Corner taps - Miller 3rd Edition
Flange taps - Miller 3rd Edition
D & D/2 taps - Miller 3rd Edition
2½ & 8D taps - Miller 3rd Edition
Segmental Orifice | Corner taps - Miller 3rd Edition
Flange taps - Miller 3rd Edition
D & D/2 taps - Miller 3rd Edition
2½ & 8D taps - Miller 3rd Edition

## Input
Fluid | Gas
Operating Pressure | 5101325 | Pa[A]
Operating Temperature | 673.15 | °K
Operating Density | 28 | kg/m3
Compressibility | 0.9
Operating Viscosity | 1e-05 | Pa.s
Isentropic Index | 1.35
Liquid Vapour Pressure |  | Pa[A]
Flowrate (x4) | 5 | kg/s
Materials | CS Pipe | 1.353e-05
Co-efficient of Expansion | 316L Element | 1.789e-05
Pipe ID | 0.20276 | m
Pipe WT | 0.00602 | m
DP | 30000 | Pa[A] | Bore | 0.087025 | m
Convert Operating Pressure | 5101325 | Pa[A]
Convert temperature | 673.15 | °K
Calculate mass flow (if not given) | 5 | kg/s
Calc/convert density | 28 | kg/m³
Convert diameter with expans. | 0.2038 | m
Calc pipe area | 0.032622 | m2
Calc pipe velocity | 5.474 | m/s
Calculate viscosity | 1e-05 | Pa.s
Calc Reynolds Number | 3123709.7938

## Concentric - Corner
CALCULATION TYPE | Miller |  |  | CH/FPD/ORIFICE/DESIGN | C1 | Concentric - Corner taps
Convert Operating Pressure | 5101325 | Pa[A]
Convert temperature | 673.15 | °K
Calculate mass flow (if not given) | 5 | kg/s
Calc/convert density | 28 | kg/m³
Convert diameter with expans. | 0.2038 | m
Calc pipe area | 0.032622 | m2
Calc pipe velocity | 5.474 | m/s
Calculate viscosity | 1e-05 | Pa.s
Calc Reynolds Number | 3123709.7938
DP | 30000 | Pa[A] |  | Operating Bore | 0.087617 | m
Downstream Pressure, P2 | 5071325 | Pa[A] |  | Beta | 0.42991
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  | Co-efficient of Discharge, C | 0.60119
Sizing Factor, SM | 0.11825 |  |  | Initial Expansibility Factor, Y0 | 1
Initial Beta, β0 | 0.43973 |  |  | Differential Pressure, Δp | 32817.7903 | Pa[A]
Co-efficient of Discharge, C0 | 0.60141 |  |  | Expansibility Factor, Y | 0.99799
Expansibility Factor, Y0 | 0.99816
Beta, β1 | 0.43963
Co-efficient of Discharge, C1 | 0.60141
Expansibility Factor, Y1 | 0.99816
Operting Bore | 0.089597 | m
Machined Bore | 0.088992 | m
Machined Bore (mm) | 88.9921 | mm |  | Differential Pressure, Δp | 32950.1666 | Pa[A]
qm | 5 | kg/s |  | qm | 5 | kg/s
Iterate until B51=B27
Device
| Corner Taps | Flange Taps | D and D/2 Taps | Units | Warning
Min bore,d | 12.5 | 12.5 | 12.5 | mm | Bore too low
Min pipe ID, D | 50 | 50 | 50 | mm | Pipe ID too low
Max pipe ID, D | 1000 | 1000 | 1000 | mm | Pipe ID too high
Min beta, β | 0.1 | 0.1 | 0.1 |  | Beta ratio too low
Max beta, β | 0.75 | 0.75 | 0.75 |  | Beta ratio too high
Min Reynolds | 5000 | 5000 AND 170β2D | 5000 | For Beta less than 0.56 | Reynolds Number too low
Min Reynolds | 16000β2 | 5000 AND 170β2D | 16000β2 | For Beta more than 0.56 | Reynolds Number too low
Max p2/p1 | 0.75 | 0.75 | 0.75 |  | Pressure drop too high
Note on A38: Jen Wilson: Miller Table 9.15

## Concentric - Flange
CALCULATION TYPE | Miller |  |  | CH/FPD/ORIFICE/DESIGN | C2 | Concentric - Flange taps
Convert Operating Pressure | 5101325 | Pa[A]
Convert temperature | 673.15 | °K
Calculate mass flow (if not given) | 5 | kg/s
Calc/convert density | 28 | kg/m³
Convert diameter with expans. | 0.2038 | m
Calc pipe area | 0.032622 | m2
Calc pipe velocity | 5.474 | m/s
Calculate viscosity | 1e-05 | Pa.s
Calc Reynolds Number | 3123709.7938
DP | 30000 | Pa[A] |  | Operating Bore | 0.087617 | m
Downstream Pressure, P2 | 5071325 | Pa[A] |  | Beta | 0.42991
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  | Co-efficient of Discharge, C | 0.6012
Sizing Factor, SM | 0.11825 |  |  | Initial Expansibility Factor, Y0 | 1
Initial Beta, β0 | 0.43973 |  |  | Differential Pressure, Δp | 32816.478 | Pa[A]
Co-efficient of Discharge, C0 | 0.60144 |  |  | Expansibility Factor, Y | 0.99799
Expansibility Factor, Y0 | 0.99816
Beta, β1 | 0.43962
Co-efficient of Discharge, C1 | 0.60143
Expansibility Factor, Y1 | 0.99816
Operting Bore | 0.089595 | m
Machined Bore | 0.08899 | m
Machined Bore (mm) | 88.9903 | mm |  | Differential Pressure, Δp | 32948.8438 | Pa[A]
qm | 5 | kg/s |  | qm | 5 | kg/s
Iterate until B51=B27
Device
| Corner Taps | Flange Taps | D and D/2 Taps | Units | Warning
Min bore,d | 12.5 | 12.5 | 12.5 | mm | Bore too low
Min pipe ID, D | 50 | 50 | 50 | mm | Pipe ID too low
Max pipe ID, D | 1000 | 1000 | 1000 | mm | Pipe ID too high
Min beta, β | 0.1 | 0.1 | 0.1 |  | Beta ratio too low
Max beta, β | 0.75 | 0.75 | 0.75 |  | Beta ratio too high
Min Reynolds | 5000 | 5000 AND 170β2D | 5000 | For Beta less than 0.56 | Reynolds Number too low
Min Reynolds | 16000β2 | 5000 AND 170β2D | 16000β2 | For Beta more than 0.56 | Reynolds Number too low
Max p2/p1 | 0.75 | 0.75 | 0.75 |  | Pressure drop too high
Note on A38: Jen Wilson: Miller Table 9.15

## Concentric - D D2
CALCULATION TYPE | Miller |  |  | CH/FPD/ORIFICE/DESIGN | C3 | Concentric - D & D/2 taps
Convert Operating Pressure | 5101325 | Pa[A]
Convert temperature | 673.15 | °K
Calculate mass flow (if not given) | 5 | kg/s
Calc/convert density | 28 | kg/m³
Convert diameter with expans. | 0.2038 | m
Calc pipe area | 0.032622 | m2
Calc pipe velocity | 5.474 | m/s
Calculate viscosity | 1e-05 | Pa.s
Calc Reynolds Number | 3123709.7938
DP | 30000 | Pa[A] |  | Operating Bore | 0.087617 | m
Downstream Pressure, P2 | 5071325 | Pa[A] |  | Beta | 0.42991
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  | Co-efficient of Discharge, C | 0.60126
Sizing Factor, SM | 0.11825 |  |  | Initial Expansibility Factor, Y0 | 1
Initial Beta, β0 | 0.43973 |  |  | Differential Pressure, Δp | 32810.1734 | Pa[A]
Co-efficient of Discharge, C0 | 0.60153 |  |  | Expansibility Factor, Y | 0.99799
Expansibility Factor, Y0 | 0.99816
Beta, β1 | 0.43959
Co-efficient of Discharge, C1 | 0.60152
Expansibility Factor, Y1 | 0.99816
Operting Bore | 0.089589 | m
Machined Bore | 0.088984 | m
Machined Bore (mm) | 88.984 | mm |  | Differential Pressure, Δp | 32942.4882 | Pa[A]
qm | 5 | kg/s |  | qm | 5 | kg/s
Iterate until B51=B27
Device
| Corner Taps | Flange Taps | D and D/2 Taps | Units | Warning
Min bore,d | 12.5 | 12.5 | 12.5 | mm | Bore too low
Min pipe ID, D | 50 | 50 | 50 | mm | Pipe ID too low
Max pipe ID, D | 1000 | 1000 | 1000 | mm | Pipe ID too high
Min beta, β | 0.1 | 0.1 | 0.1 |  | Beta ratio too low
Max beta, β | 0.75 | 0.75 | 0.75 |  | Beta ratio too high
Min Reynolds | 5000 | 5000 AND 170β2D | 5000 | For Beta less than 0.56 | Reynolds Number too low
Min Reynolds | 16000β2 | 5000 AND 170β2D | 16000β2 | For Beta more than 0.56 | Reynolds Number too low
Max p2/p1 | 0.75 | 0.75 | 0.75 |  | Pressure drop too high
Note on A38: Jen Wilson: Miller Table 9.15

## Concentric - 2.5 8D
CALCULATION TYPE | Miller |  |  | CH/FPD/ORIFICE/DESIGN | C4 | Concentric - 2½ & 8D taps
Convert Operating Pressure | 5101325 | Pa[A]
Convert temperature | 673.15 | °K
Calculate mass flow (if not given) | 5 | kg/s
Calc/convert density | 28 | kg/m³
Convert diameter with expans. | 0.2038 | m
Calc pipe area | 0.032622 | m2
Calc pipe velocity | 5.474 | m/s
Calculate viscosity | 1e-05 | Pa.s
Calc Reynolds Number | 3123709.7938
DP | 30000 | Pa[A] |  | Operating Bore | 0.087617 | m
Downstream Pressure, P2 | 5071325 | Pa[A] |  | Beta | 0.42991
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  | Co-efficient of Discharge, C | 0.6763
Sizing Factor, SM | 0.11825 |  |  | Initial Expansibility Factor, Y0 | 1
Initial Beta, β0 | 0.41539 |  |  | Differential Pressure, Δp | 25933.0647 | Pa[A]
Co-efficient of Discharge, C0 | 0.67051 |  |  | Expansibility Factor, Y | 0.9979
Expansibility Factor, Y0 | 0.99764 |  |  | Differential Pressure, Δp | 26042.1217 | Pa[A]
Beta, β1 | 0.41722 |  |  | Expansibility Factor, Y | 0.9979
Co-efficient of Discharge, C1 | 0.67123
Expansibility Factor, Y1 | 0.99764
Beta, β2 | 0.41701
Co-efficient of Discharge, C2 | 0.67115
Expansibility Factor, Y2 | 0.99764
Operting Bore | 0.084988 | m
Machined Bore | 0.084414 | m
Machined Bore (mm) | 84.414 | mm |  | Differential Pressure, Δp | 26042.5818 | Pa[A]
qm | 5.0002 | kg/s |  | qm | 5 | kg/s
Iterate until B51=B27
Device
| Corner Taps | Flange Taps | D and D/2 Taps | Units | Warning
Min bore,d | 12.5 | 12.5 | 12.5 | mm | Bore too low
Min pipe ID, D | 50 | 50 | 50 | mm | Pipe ID too low
Max pipe ID, D | 1000 | 1000 | 1000 | mm | Pipe ID too high
Min beta, β | 0.1 | 0.1 | 0.1 |  | Beta ratio too low
Max beta, β | 0.75 | 0.75 | 0.75 |  | Beta ratio too high
Min Reynolds | 5000 | 5000 AND 170β2D | 5000 | For Beta less than 0.56 | Reynolds Number too low
Min Reynolds | 16000β2 | 5000 AND 170β2D | 16000β2 | For Beta more than 0.56 | Reynolds Number too low
Max p2/p1 | 0.75 | 0.75 | 0.75 |  | Pressure drop too high
Note on A38: Jen Wilson: Miller Table 9.15

## Conical
CALCULATION TYPE | Miller |  |  | CH/FPD/ORIFICE/DESIGN | L1 | Conical entrance - Corner taps
Convert Operating Pressure | 5101325 | Pa[A]
Convert temperature | 673.15 | °K
Calculate mass flow (if not given) | 5 | kg/s
Calc/convert density | 28 | kg/m³
Convert diameter with expans. | 0.2038 | m
Calc pipe area | 0.032622 | m2
Calc pipe velocity | 5.474 | m/s
Calculate viscosity | 1e-05 | Pa.s
Calc Reynolds Number | 3123709.7938
DP | 30000 | Pa[A] |  | Operating Bore | 0.087617 | m
Downstream Pressure, P2 | 5071325 | Pa[A] |  | Beta | 0.42991
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  | Co-efficient of Discharge, C | 0.73
Sizing Factor, SM | 0.11825 |  |  | Initial Expansibility Factor, Y0 | 1
Initial Beta, β0 | 0.39882 |  |  | Differential Pressure, Δp | 22257.7163 | Pa[A]
Co-efficient of Discharge, C0 | 0.73 |  |  | Expansibility Factor, Y1 | 0.99818
Expansibility Factor, Y0 | 0.99818
Beta, β1 | 0.40024
Co-efficient of Discharge, C1 | 0.73
Expansibility Factor, Y1 | 0.99817
Operting Bore | 0.081569 | m
Machined Bore | 0.081018 | m
Machined Bore (mm) | 81.0183 | mm |  | Differential Pressure, Δp | 22339.162 | Pa[A]
qm | 5 | kg/s |  | qm | 5 | kg/s
Iterate until B45=B27
Device
|  | Units | Warning
Min bore,d | 6 | mm | Bore too low
Min pipe ID, D | 50 | mm | Pipe ID too low
Max pipe ID, D | 500 | mm | Pipe ID too high
Min beta, β | 0.1 |  | Beta ratio too low
Max beta, β | 0.316 |  | Beta ratio too high
Min Reynolds | 80 |  | Reynolds Number too low
Max Reynolds | 2*105*beta |  | Reynolds Number too high
Max p2/p1 | 0.75 |  | Pressure drop too high
Note on A38: Jen Wilson: Miller Table 9.15

## Eccentric
Eccentric Orifice | Eccentric - Flange taps 90° | CH/FPD/ORIFICE/DESIGN | E2 | Eccentric - Flange taps 90°
|  |  | E3 | Eccentric - Flange taps 180°
[5 empty] | a | b | c | d | e | f | g | h | i | j
Convert Operating Pressure | 5101325 | Pa[A] | D≤100mm | Eccentric - Flange taps 90° | 0.5917 | 0.3061 | 0.3406 | -0.1019 | -0.2715 | 7.3 | -15.7 | 170.8 | -399.7 | 332.2
Convert temperature | 673.15 | °K | D≤100mm | Eccentric - Flange taps 180° | 0.5866 | 0.3917 | 0.7586 | -0.2273 | -0.3343 | 69.1 | -469.4 | 1245.6 | -1287.5 | 486.2
Calculate mass flow (if not given) | 5 | kg/s |  |  | 0.5917 | 0.3061 | 0.3406 | -0.1019 | -0.2715 | 7.3 | -15.7 | 170.8 | -399.7 | 332.2
Calc/convert density | 28 | kg/m³
Convert diameter with expans. | 0.2038 | m | D>100mm | Eccentric - Flange taps 90° | 0.6016 | 0.3312 | -1.5581 | 0.651 | -0.7308 | -139.7 | 1328.8 | -4228.2 | 5691.9 | -2710.4
Calc pipe area | 0.032622 | m2 | D>100mm | Eccentric - Flange taps 180° | 0.6037 | 0.1598 | -0.2918 | 0.0244 | -0.079 | -103.2 | 898.3 | -2557.3 | 2977 | -1131.3
Calc pipe velocity | 5.474 | m/s |  |  | 0.6016 | 0.3312 | -1.5581 | 0.651 | -0.7308 | -139.7 | 1328.8 | -4228.2 | 5691.9 | -2710.4
Calculate viscosity | 1e-05 | Pa.s
Calc Reynolds Number | 3123709.7938 |  |  |  | 0.6016 | 0.3312 | -1.5581 | 0.651 | -0.7308 | -139.7 | 1328.8 | -4228.2 | 5691.9 | -2710.4
DP | 30000 | Pa[A] |  | Operating Bore | a: 0.087617; b: m
Downstream Pressure, P2 | 5071325 | Pa[A] |  | Beta | a: 0.42991
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  | Co-efficient of Discharge, C | a: 0.6189
Sizing Factor, SM | 0.11825 |  |  | Initial Expansibility Factor, Y0 | bar: a
Initial Beta, β0 | 0.43372 |  |  | Differential Pressure, Δp | a: 30965.5749; b: Pa[A]
Co-efficient of Discharge, C0 | 0.6191 |  |  | Expansibility Factor, Y | a: 0.99818
Expansibility Factor, Y0 | 0.99823
Beta, β1 | 0.43351
Operting Bore | 0.088351 | m
Machined Bore | 0.087755 | m
Machined Bore (mm) | 87.7547 | mm |  | Differential Pressure, Δp | a: 31078.6464; b: Pa[A]
Iterate until B55=B27
qm | 5 | kg/s |  | qm | a: 5; b: kg/s
Device
| Corner Taps | Units | Warning
Min bore,d | 50 | mm | Bore too low
Min pipe ID, D | 100 | mm | Pipe ID too low
Max pipe ID, D | 1000 | mm | Pipe ID too high
Min beta, β | 0.46 |  | Beta ratio too low
Max beta, β | 0.84 |  | Beta ratio too high
Min Reynolds | 2x105β2 |  | Reynolds Number too low
Max Reynolds | 106β |  | Reynolds Number too high
Max p2/p1 | 0.75 |  | Pressure drop too high
Note on A38: Jen Wilson: Miller Table 9.15

## Quarter Circle
CALCULATION TYPE | Miller |  |  | CH/FPD/ORIFICE/DESIGN | Q1 | Quarter circle - Corner taps
[5 empty] | Q2 | Quarter circle - Flange taps
Convert Operating Pressure | 5101325 | Pa[A]
Convert temperature | 673.15 | °K
Calculate mass flow (if not given) | 5 | kg/s
Calc/convert density | 28 | kg/m³
Convert diameter with expans. | 0.2038 | m
Calc pipe area | 0.032622 | m2
Calc pipe velocity | 5.474 | m/s
Calculate viscosity | 1e-05 | Pa.s
Calc Reynolds Number | 3123709.7938
DP | 30000 | Pa[A] |  | Operating Bore | 0.087617 | m
Downstream Pressure, P2 | 5071325 | Pa[A] |  | Beta | 0.42991
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  | Co-efficient of Discharge, C | 0.78668
Sizing Factor, SM | 0.11825 |  |  | Initial Expansibility Factor, Y0 | 1
Initial Beta, β0 | 0.38458 |  |  | Differential Pressure, Δp | 19165.7817 | Pa[A]
Co-efficient of Discharge, C0 | 0.78084 |  |  | Expansibility Factor, Y | 0.99883
Expansibility Factor, Y0 | 0.99818
Beta, β1 | 0.3873
Operting Bore | 0.078933 | m
Machined Bore | 0.0784 | m
Machined Bore (mm) | 78.3998 | mm |  | Differential Pressure, Δp | 19210.8736 | Pa[A]
Iterate until B55=B27
qm | 5 | kg/s |  | qm | 5 | kg/s
Device
| Corner Taps | Units | Warning
Min bore,d | 15 | mm | Bore too low
Min pipe ID, D | - | mm | Pipe ID too low
Max pipe ID, D | 500 | mm | Pipe ID too high
Min beta, β | 0.245 |  | Beta ratio too low
Max beta, β | 0.6 |  | Beta ratio too high
Min Reynolds | 1000β +9.4x106(β-0.24)8 |  | Reynolds Number too low
Max Reynolds | 105β |  | Reynolds Number too high
Max p2/p1 | 0.75 |  | Pressure drop too high
Note on A38: Jen Wilson: Miller Table 9.15

## Segmental
CALCULATION TYPE | Miller |  |  | CH/FPD/ORIFICE/DESIGN | S2 | Segmental - Flange taps
Convert Operating Pressure | 5101325 | Pa[A]
Convert temperature | 673.15 | °K
Calculate mass flow (if not given) | 5 | kg/s
Calc/convert density | 28 | kg/m³
Convert diameter with expans. | 0.2038 | m
Calc pipe area | 0.032622 | m2 |  |  | a | b | c | d | e
Calc pipe velocity | 5.474 | m/s | D≤100mm | Flange taps - Miller 3rd Edition | 0.6284 | 0.1462 | -0.8464 | 0.2603 | -0.2886
Calculate viscosity | 1e-05 | Pa.s | D>100mm | Flange taps - Miller 3rd Edition | 0.6276 | 0.0828 | 0.2739 | -0.0934 | -0.1132
Calc Reynolds Number | 3123709.7938 |  |  |  | 0.6276 | 0.0828 | 0.2739 | -0.0934 | -0.1132
DP | 30000 | Pa[A] |  | Operating Bore | 0.087617 | m
Downstream Pressure, P2 | 5071325 | Pa[A] |  | Beta | 0.42991
N Factor for Mass Flow, N*Mρ | 3.5124e-05 | [kg/s] |  | Co-efficient of Discharge, C | 0.62969
Sizing Factor, SM | 0.11825 |  |  | Initial Expansibility Factor, Y0 | 1
Initial Beta, β0 | 0.43061 |  |  | Differential Pressure, Δp | 29914.2415 | Pa[A]
Co-efficient of Discharge, C0 | 0.62967 |  |  | Expansibility Factor, Y | 0.99847
Expansibility Factor, Y0 | 0.99847
Beta, β1 | 0.42994
Operting Bore | 0.087622 | m
Machined Bore | 0.087031 | m
Machined Bore (mm) | 87.0306 | mm |  | Differential Pressure, Δp | 30005.9587 | Pa[A]
Iterate until B55=B27
qm | 5 | kg/s |  | qm | 5 | kg/s
Device
| Corner Taps | Units | Warning
Min bore,d | 50 | mm | Bore too low
Min pipe ID, D | 100 | mm | Pipe ID too low
Max pipe ID, D | 1000 | mm | Pipe ID too high
Min beta, β | 0.46 |  | Beta ratio too low
Max beta, β | 0.84 |  | Beta ratio too high
Min Reynolds | 2x105β2 |  | Reynolds Number too low
Max Reynolds | 106β |  | Reynolds Number too high
Max p2/p1 | 0.75 |  | Pressure drop too high
Note on A38: Jen Wilson: Miller Table 9.15